##### To be inserted into Section 15700 – Hydronic System

- Combination Actuated Ball Valves and Flow Limiting Cartridge (Automizer)

  - Combination valve shall include a Flow Limiting Cartridge, Actuated Ball Valve, and Manual Isolation Ball in a single valve housing.

  - Valve housing shall consist of forged brass, rated at no less than 360 psi at 250(F.

  - Valve shall have a union end connection that includes a factory installed manual air vent to allow for venting of the coil or heat pump.

  - Automatic Flow Limiting Cartridge (FLC)

    - FLC shall automatically control flow rates with (5% accuracy over an operating pressure differential range of at least 14 times the minimum required for control.  Three operating pressure ranges shall be available with the minimum range requiring less than 3 PSID to actuate the mechanism.

    - Valve internal control mechanism shall consist of a stainless steel one-piece cartridge with segmented port design and full travel linear coil spring.

    - Dual pressure/temperature test valves for verifying the pressure differential across the cartridge and system shall be standard.

    - Manufacturer shall be able to provide certified independent laboratory tests verifying accuracy of performance

  - Actuated Ball Valve

    - Valve ball shall consist of chemically plated nickel brass.

    - Actuator stem shall be removable/replaceable without removing valve from line.

    - Manufacturer shall be able to provide ball insert to make flow control equal percentage.

    - Valve shall have EPDM O-Rings behind ball seals to allow for a minimum close-off pressure of 100 psi with 35 in-lbs of torque for 1/2" to 1-1/2" sizes.

    - Actuator shall provide minimum torque required for full valve shutoff position.

  - Isolation Ball Valve

    - Valve shall include a 600 WOG manual isolation ball valve.

- Warranty

  - All components shall be warranted by manufacturer for no less than one year from date of purchase. The flow limiting cartridge shall be warranted by manufacturer for no less than five years from date of purchase.

##### To be inserted into Section 15970 – Energy Management & Controls or Section 17000 – Building Automation

- All valves for individual coil controls shall be provided as part of Hydronic Coil Piping  / Hose Kit Packages as specified in section 15700.  The contractor may be responsible for all actuators for all valves, which may be shipped to the valve manufacturer as an option for factory installation.